## Slide 1: Operations & Maintenance Report – July 2020

## Slide 2
June Plant Performance

## Slide 3
June Resource Recovery

## Slide 4
What’s happened in
. . . so far.
July

## Slide 5: Badfish Creek Forcemain TFO Summary

## Slide 6
Badfish Creek FM TFO Summary
Leak discovered on the south side of the meter vault (concrete structure above)
Disinfected treated effluent flowed along curb into the storm water system

## Slide 7
Contractor excavating where pooling water was found.
Dig site quickly filling with treated effluent.
Badfish Creek FM TFO Summary

## Slide 8
Excavation revealed leak was coming from the bottom of a capped wye section of forcemain.
Dewatering pumps needed for access to leaking pipe fitting.
Badfish Creek FM TFO Summary

## Slide 9
Closeup of leaking piping fitting at bottom of cap. Mortar encasing pipe has been removed.
Pipe fittings likely used for pressure testing during construction.
Badfish Creek FM TFO Summary

## Slide 10
Closeup of corroded pipe fittings. Pipe is 6” long, 2” diameter
Badfish Creek FM TFO Summary

## Slide 11
Contractor completed repairs. Mortar covered plug can be seen at top of cap.
Badfish Creek FM TFO Summary

## Slide 12: Septage Receiving TFO Summary

## Slide 13
Septage Receiving TFO Summary
Source of the TFO. Drainage pipe had not been capped following disconnection.

## Slide 14
Septage Receiving TFO Summary
Spilled septage material accumulated in the contractor’s excavation site.

## Slide 15
Septage Receiving TFO Summary
Line was capped to prevent further overflow.
Septage receiving station in background.

## Slide 16
Struvite Harvesting
Conveyor

## Slide 17
Struvite Harvesting
Conveyor

## Slide 18: Operations & Maintenance
Did you know?
How many maintenance hours were dedicated to preventative maintenance in 2019?
22,815 hours
*Equivalent to approximately 13 workers 100% dedicated actual work hours.

## Slide 19
Thank you!